## Slide 1
Data Analytics for Securing Fault Localization Applications
Teklemariam Tesfay, Anna Scaglione
Fault detectors are vulnerable
PMU DATA FOR FAULT LOCALIZATION
Collaboration Opportunities
Compare fault localization results that use data from a limited number of PMUs with results from fault detectors data analytics to detect the presence of a cyber attack.
Zone identification
Cyber attack detection
Faults happen due to natural effects, man-made situations, or from equipment failures
Data from fault detectors allow fast fault detection and localization
An attacker can manipulate the SCADA data from fault detectors to give wrong fault location or hide its presence, thereby delaying service restoration
Analyzing aggregated data from multiple PMUs to localize fault
Only few PMU deployed (economics!) forcing utilities to operate in low measurement regime
Not enough to pinpoint the exact location of a fault
Proposed formulation
Localizes a fault with low resolution about the exact location
Uses pre- and post-fault data and bus admittance matrix
Tested on an IEEE-34 bus system using OpenDSS to generate simulated pre- and post-fault data.
This research would benefit from collaboration with industry partners in the following areas:
Datasets of PMU measurements and SCADA data from actual distribution systems
Industry level implementation for DMS to commercialize our solution
Contact: Anna.Scaglione@asu.edu, ttesfay@asu.edu
Activity webpage: https://cred-c.org/researchactivity/Analytics
Fault Type | Exact fault location | Highly probably faulty nodes
LLL | 816 | 814,816,850
A-G | 822-A | 814-A,816-A,818-A,820-A,822-A,850-A
BC-G | 852-B-C | 832-B-C,852-B-C
Future Direction
Mathematical formulation for optimal PMU placement guaranteeing minimum ambiguity throughout the network
Implement the proposed method on SPARCS architecture
Simulation results show the presence of a cluster of nodes (communities) as candidate fault locations
Nodes that have similar properties in the fault localization application (that have strong correlation) form a zone
The size and structure of the zones are dependent on the network topology and the placement of PMUs
Proposed a placement heuristics guaranteeing balanced zone sizes
Zones are formed by neighboring nodes in a network
IMPACT on state of Grid security
Impacts on Your Grid
Prevent delayed recovery from a fault that could be caused as a result of a cyber attack that mis-locates or hides the fault
Business Benefits
Economic placement of PMUs
Minimize economic lose by enabling fast isolation of fault locations
Simulated SCADA data for fault detectors at each end of the lines is generated using opendnp3.
A-G fault introduced at 822-A
PMU data analytics shows fault in buses 814-A,816-A,818-A,820-A,822-A,850-A (Zone B)
Simulated SCADA data from fault detectors manipulated such that the analytics shows fault at 846-A (Zone D)
Inconsistent results. Alarm about presence of a cyber attack!
Actual
fault location
Fault location from manipulated data
Faulty Zone identified using μPMU data analytics
A
B
C
D
E
Research vision
SPARCS hierarchical architecture
Correlation coefficients heat-map
Local PMU data analytics
Local SCADA data analytics
Cassandra /Elastic Search Databases
Central PMU analytics
Central SCADA data analytics
…
Check for inconsistency
…
PMU
Fault detector
010…
Attacker